## Table 1 A & B
Table 1A. Data Summary Part A
[6 empty] | Q | Wfuel | MCave | Qin | Qout
Category | Run No. | Load % Capacity | Target Load | Actual Load | Actual Load | Test Duration | Wood Weight as-fired | Wood Moisture | Heat Input | Heat Output
|  |  | Btu/hr | Btu/hr | % of Max | hrs | lb | % DB | Btu | Btu
I |  | <15% of Max | 51000 | 46531.2151 | 13.69% | 28.7 | 257.21 | 21.37 | 1822491.3984 | 1335445.8743 | 0%
II |  | 16-24% of Max | 81600 | 74299.9214 | 21.85% | 17.8833 | 252.44 | 22.58 | 1771100.3323 | 1328730.2608 | 0%
III |  | 25-50% of max | 170000 | 152496.0924 | 44.85% | 8.75 | 248.22 | 21.62 | 1755271.3346 | 1334340.8086 | 0%
IV |  | Max capacity | 340000 | 335009.7094 | 98.53% | 3.8333 | 258.04 | 23.71 | 1793777.4992 | 1284203.8862 | 0%
Table 1B. Data Summary Part B
|  |  | T2 Min | ET | E | E | Eg/hr | Eg/kg | hdel | hSLM
Category | Run No. | Load % Capacity | Min Return Water Temp. | Total PM Emissions | PM Output Based | PM Output Based | PM Rate | PM Factor | Delivered Efficiency | Stack Loss Efficiency
|  |  | ºF | g | lb/mmBtu Out | g/MJ | g/hr | g/kg | % | %
I |  | <15% of Max | 154.3 | 121.8323 | 0.20113 | 0.086474 | 4.245 | 1.2671 | 73.28% | 60.2%
II |  | 16-24% of Max | 153.99 | 204.6389 | 0.33954 | 0.14598 | 11.443 | 2.1901 | 75.02% | *
III |  | 25-50% of max | 148.5 | 124.2452 | 0.20528 | 0.088259 | 14.1994 | 1.3417 | 76.02% | 57.1%
IV |  | Max capacity | 127.66 | 42.3056 | 0.072627 | 0.031226 | 11.0362 | 0.44703 | 71.59% | 85.2%
* NOTE: An anomaly was seen in the measured CO numbers. CO exceeded 7.0% on several occasions and even achieved over 10%; therefore, the resulting stack loss efficiency calculation was showing a -240%.

## Hang Tag Info
Table 1C: Hang Tag Information
MANUFACTURER: | SteelTech
MODEL NUMBER: | G400
8-HOUR OUTPUT RATING: | Qout-8hr | 180409 | Btu/hr
8-HOUR AVERAGE EFFICIENCY: | havg-8hr | 74.8% | (Using higher heating value)
|  | 80.5% | (using lower heating value)
ANNUAL EFFICIENCY RATING: | havg | 74.36% | (Using higher heating value)
|  | 80.06% | (using lower heating value)
PARTICULATE EMISSIONS: | Eavg | 9.0352 | GRAMS/HR (average)
|  | 0.22879 | LBS/MILLION Btu OUTPUT

## Yr Rnd Weighted
Table 2. Year Round Use Weighting
Category | Run No. | Weighting Factor | hdel,i x Fi-HHV | hdel,i x Fi-LHV | Eg/MJ,i x Fi | Eg/kg,i x Fi | Elb/mmbtu,i x Fi | Eg/hr,i x Fi
I |  | 0.437 | 0.32022 | 0.34479 | 0.037789 | 0.55372 | 0.087893 | 1.8551
II |  | 0.238 | 0.17855 | 0.19223 | 0.034744 | 0.52123 | 0.08081 | 2.7234
III |  | 0.275 | 0.20905 | 0.22507 | 0.024271 | 0.36896 | 0.056452 | 3.9048
IV |  | 0.05 | 0.035796 | 0.038539 | 0.0015613 | 0.022352 | 0.0036314 | 0.55181
Totals |  | 1 | 74.36% | 80.06% | 0.098365 | 1.4663 | 0.22879 | 9.0352